## raw data (hidden)
|  | Deep Seated | Surface Fire |  |  |  |  | Material | Minimum Design Co2 Concentration ( % ) |  | Material | Minimum Design Co2 Concentration ( % ) |  | Material | Minimum Design Co2 Concentration ( % ) |  | Material Conversion Factor (BS5839-4, Table 2) |  | Material Conversion Factor
Deep Seated | NFPA 12 | 7 min. | 2 min. | 7 min. | 7 | 1 | Yes | Acetylene | 66 | 0 | Acetylene | 66 | 0 | Acetylene | 66 | 0 | 2.5 | 0 | Methane
Surface Fire | Vds 2093 | 7 min. (30% in 2 min.) | 1 min. | 7 min. (30% in 2 min.) | 8 | 2 | No | Acetone | 34 | 0 | Acetone | 34 | 0 | Acetone | 31 | 0 | 1 | 0 | Methane
| ISO 6183 | 4 min. |  | 4 min. | 4 | 3 |  | Aviation Gas Grades 115/145 | 36 | 0 | Aviation Gas Grades 115/145 | 36 | 0 | Benzol, benzene | 37 | 0 | 1.1 | 0
| BS 5306 - 4 | 3 min. |  | 3 min. | 3 | 4 |  | Benzol, benzene | 37 | 0 | Benzol, benzene | 37 | 0 | Butane | 34 | 0 | 1 | 0
|  | 2 min. |  | 2 min. | 2 | 5 |  | Buta diene | 41 | 0 | Buta diene | 41 | 0 | Butane-I, 3-diene | 41 | 0 | 1.3 | 0
|  | 1 min. |  | 1 min. | 1 |  |  | Butane | 34 | 0 | Butane | 34 | 0 | Carbon Disulphide | 72 | 0 | 3 | 0
[8 empty] | Butane-I | 37 | 0 | Butane-I | 37 | 0 | Carbon monoxide | 64 | 0 | 2.4 | 0
[8 empty] | Carbon Disulphide | 72 | 0 | Carbon Disulphide | 72 | 0 | Coal gas or natural gas | 37 | 0 | 1.1 | 0
[8 empty] | Carbon monoxide | 64 | 0 | Carbon monoxide | 64 | 0 | Cyclopropane | 37 | 0 | 1.1 | 0
[8 empty] | Coal gas or natural gas | 37 | 0 | Coal gas or natural gas | 37 | 0 | Diethyl Ether | 46 | 0 | 1.5 | 0
[8 empty] | Cyclopropane | 37 | 0 | Cyclopropane | 37 | 0 | Dowtherm | 46 | 0 | 1.5 | 0
[8 empty] | Diethyl Ether | 40 | 0 | Diethyl Ether | 40 | 0 | Ethane | 40 | 0 | 1.2 | 0
[8 empty] | Dimethyl Ether | 40 | 0 | Dimethyl Ether | 40 | 0 | Ethyle Alcohole(Ethanol) | 43 | 0 | 1.3 | 0
[8 empty] | Dowtherm | 46 | 0 | Dowtherm | 46 | 0 | Ethylene | 49 | 0 | 1.6 | 0
[8 empty] | Ethane | 40 | 0 | Ethane | 40 | 0 | Ethylene dichloride | 25 | 0 | 1 | 0
[8 empty] | Ethyle Alcohole (Ethanol) | 43 | 0 | Ethyle Alcohole (Ethanol) | 43 | 0 | Ethylene oxide | 53 | 0 | 1.75 | 0
[8 empty] | Ethyle Ether | 46 | 0 | Ethyle Ether | 46 | 0 | Hexane | 35 | 0 | 1.1 | 0
[8 empty] | Ethylene | 49 | 0 | Ethylene | 49 | 0 | Hydrogen | 75 | 0 | 3.3 | 0
[8 empty] | Ethylene dichloride | 25 | 0 | Ethylene dichloride | 25 | 0 | Isobutane | 36 | 0 | 1.1 | 0
[8 empty] | Ethylene oxide | 53 | 0 | Ethylene oxide | 53 | 0 | Kerosene | 34 | 0 | 1 | 0
[8 empty] | Gasoline | 34 | 0 | Gasoline | 34 | 0 | Methane | 34 | 34 | 1 | 1
[8 empty] | Hexane | 35 | 0 | Hexane | 35 | 0 | Methyl Alcohole(Methanol) | 40 | 0 | 1.2 | 0
[8 empty] | Higher Paraffin Hydrocarbon | 34 | 0 | Higher Paraffin Hydrocarbon | 34 | 0 | Pentane | 35 | 0 | 1.1 | 0
[8 empty] | Hydrogen | 75 | 0 | Hydrogen | 75 | 0 | Petroleum Spirit | 34 | 0 | 1 | 0
[8 empty] | Hydrogen Sulfide | 36 | 0 | Hydrogen Sulfide | 36 | 0 | Propane | 36 | 0 | 1.1 | 0
[8 empty] | Isobutane | 36 | 0 | Isobutane | 36 | 0 | Propene | 36 | 0 | 1.1 | 0
[8 empty] | Isobutylene | 34 | 0 | Isobutylene | 34 | 0 | Quenching, lubricating oils | 34 | 0 | 1 | 0
[8 empty] | Isobutyl formate | 34 | 0 | Isobutyl formate | 34 | 0 |  |  |  |  | 1
[8 empty] | JP 4 | 36 | 0 | JP 4 | 36 | 0
[8 empty] | Kerosene | 34 | 0 | Kerosene | 34 | 0
[8 empty] | Methane | 34 | 34 | Methane | 34 | 34
[8 empty] | Methyl Acetate | 35 | 0 | Methyl Acetate | 35 | 0
[8 empty] | Methyl Alcohole (Methanol) | 40 | 0 | Methyl Alcohole (Methanol) | 40 | 0
[8 empty] | Methyl Butene - I | 36 | 0 | Methyl Butene - I | 36 | 0
[8 empty] | Methyl Ethyl Ketone | 40 | 0 | Methyl Ethyl Ketone | 40 | 0
[8 empty] | Methyl Ethyl formate | 39 | 0 | Methyl Ethyl formate | 39 | 0
[8 empty] | Pentane | 35 | 0 | Pentane | 35 | 0
[8 empty] | Propane | 36 | 0 | Propane | 36 | 0
[8 empty] | Propylene | 36 | 0 | Propylene | 36 | 0
[8 empty] | Quenching, lubricating oils | 34 | 0 | Quenching, lubricating oils | 34 | 0
[8 empty] | Other | 0 | 0 | Other
34
Note on J24: CnH2m + 2m - 5
Note on M24: CnH2m + 2m - 5

## Introduction
1396/05/28 | Date:
26.8 | Revision
Ali Cheraghi
یا حق
مقدمه
1. این نرم افزار کوچک آموزشی اولین بار در سال 1388 در شرکت نور ندا سیستم و بجهت آموزش پرسنل تهیه گردید و سپس در سال های بعد اصلاحاتی در آن بوجود آمد. 2. این افزار کوچک قادر به محاسبه اولیۀ حجم گاز و تعداد کپسول های محتوی گاز دی اکسید کربن (CO2)، مورد نیاز در سیستم های اطفاء حریق اتوماتیک پایۀ گاز می باشد. 3. هدف از ایجاد این نرم افزار آموزش محاسبۀ حجم گاز، سرعت بخشیدن به محاسبۀ اولیۀ حجم گاز و تعداد کپسول های مورد نیاز می باشد. 4. محاسبات نهایی و اصلی می بایست توسط نرم افزارهای مربوطه همانند نرم افزارهای شرکت TYCO-THORN-LPG انجام شود. 5. استفاده از این نرم افزار نیازمند آشنایی کامل با استاندادرهای مربوطه همانند NFPA12 و سایر کدها و الزمات مربوطه می باشد. 6. انجام محاسبات باید توسط افراد آشنا با مهندسی حریق و آموزش دیده انجام شود. 7. در صفحه خلاصه (summary)، سلول های خالی با فونت بنفش رنگ و در سایر صفحات، سلول های با فونت سبز و بنفش رنگ جهت ورود اطلاعات (اعم از تایپ و یا انتخاب گزینه) در نظر گرفته شده اند. 8. در تمامی صفحات سلول های با فونت آبی رنگ نتایج محاسبات بوده و غیر قابل تغییر می باشند. 9. برای هر بار محاسبه، صفحات باید بترتیب مرور و اطلاعات لازم در هر سطر بترتیب از بالا به پایین تکمیل شوند. 10. به هشدارهای داده شده و یا اطلاعات تکمیلی (comment) ارائه شده، توجه کامل شود.
از جناب استاد مهندس مرتضی خلیل پیما، مدیریت محترم عامل شرکت نور ندا بعلت آموزش ها و راهنمایی های همیشگی شان در مسیر آشنایی با مهندسی حریق، کمال تشکر و قدردانی را دارم. از جناب آقای مهندس امیر خلیل پیما، مدیریت محترم عامل شرکت نور ندا سیستم بعلت مساعدت و پشتیبانی همه جانبه در جهت آموزش و همچنین ایجاد این نرم افزار و سایر مقالات مزتبط با مباحث مهندسی سپاسگذارم. این نرم افزار کوچک وقف عام بوده و استفاده از آن با ذکر منبع برای تمامی افراد و سازمان ها بلامانع می باشد. از تمامی دوستان، اساتید و کارشناسان محترم تقاضا دارم تا پس از استفاده از این نرم افزار، با ارائه انتقادات، پیشنهادات و راهنمائی های خود اینجانب را در برطرف نمودن ایرادات موجود و ارتقاء این نرم افزار یاری فرمایند.
شاد زی ، مهر افزون
علی چراغی
(تهران سوم اردیبهشت (اَشَه) 1396)
راه های تماس:
| ali@noorneda.com ali_cheraghi@yahoo.com | Email:
| +98 912 376 1057 | Cellphone:
آشنایی با سیستم اطفاء حریق اتوماتیک پایۀ گاز دی اکسیدکربن

## Summary
[7 empty] | Date: | 1396/05/28
[7 empty] | Revision | 26.8
Ali Cheraghi
CO2 Fire Suppression System
Total Flooding method
Project Information
Project Name | Insert Project Name Sample |  |  |  | DATE | 1391/08/08
Contractor
Tel : |  |  |  |  | Contact
Fax :
Address
Designer |  |  |  |  | Title
Insert Data
Attention:
This Software designed for CO2 basic PreCalculation. Final Calculation Must be done by Specialist Technicians via Specified Tyco, THORN or LPG Software Programs.
Agent Calculation Result
Total quantity of CO2 required |  | 2793 | Kg
Number of Container requierd |  | 63 |  | 67 Liter Cylinders contain 45 kg CO2 (filling density: 0.67 kg/liter)
|  | #NAME? |  | Just Main Cylinders
Number of "S" Nozzels requierd |  | 26
#VALUE!

## Protected Areas
[13 empty] | Date: | 1396/05/28
[13 empty] | Revision | 26.8
Ali Cheraghi
CO2 Fire Suppression System | [14 empty] | back to Summary
Total Flooding method | [14 empty] | go to Flow Rate
Insert Project Name Sample
Design Standard |  | NFPA 12
Type of Fire |  | Deep Seated |  |  |  | NFPA 12, 5.2.3: Deep-seated fires involving solids subject to smoldering
1
Discharge Time |  | 7 min. (30% in 2 min.) |  |  |  | NFPA 12, 5.5.2.3: For deep-seated fires, the design concentration shall be achieved within 7 minutes, but the rate shall be not less than that required to develop a concentration of 30 percent in 2 minutes. (30% = 0,67 kg/m³) (also BS 5306-4, 10.6.1).
|  | 1 | 0
Design Concentration |  | 50 |  | %
Flooding Factor (F.F.) |  | 1.33 |  | Kg Co2/m3 | [5 empty] | Flooding Factor (F.F.) |  | 0 | Kg Co2/m3
Number of Enclosures |  | 3 | [8 empty] | Total Volume |  | 2100 | m3
Sector No. | Hazard Name |  | Hazard Dimension |  |  | Hazard Boundary Area | Hazard Area | Hazard Volume | Non-permeable Volume | Total Hazard Volume | Percent of Hazard Volume/Total | Flooding Factor | Basic Aget Quantity | Total Aget Quantity
|  |  | Length | Width | Height
|  |  | m | m | m | m2 | m2 | m3 | m3 | m3 | % | Kg CO2/m3 | kg | kg
1 | Switchgear Room |  | 30 | 10 | 5 | 1000 | 300 | 1500 | 75 | 1425 | 67.86% | 1.33 | 1895.25 | 1895.25
2 | Transformer Room |  | 5 | 3 | 5 | 110 | 15 | 75 | 0 | 75 | 3.571% | 1.33 | 99.75 | 99.75
3 | Cable Gallery |  | 30 | 10 | 2 | 760 | 300 | 600 | 0 | 600 | 28.57% | 1.33 | 798 | 798
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 1.33 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 1.33 | 0 | 0
[10 empty] | Q1= | Total Basic Agent |  | 2793 | kg
Select Type of Fule |  | Methane | [8 empty] | Fule Min. Design Concentration |  | 34 | %
|  | NFPA 12 |  | BS 5306
[11 empty] | Min. Design Concentration |  | 34 | %
Material Conversion Factor |  | 1 | 0 | Kg Co2/m4 | [5 empty] | Q2= | Agent |  | 2793 | kg
Leakage Compensation |  | No |  |  | 0 | [5 empty] | Compensated Agent |  | 0 | kg
[10 empty] | Q3= | Agent (+Leakage Comp.) |  | 2793 | kg
Ventilation Compensat. |  | No |  |  | 0
Ventilation Sysetm |  | 0 |  | m3/min. | [6 empty] | Compensated Agent |  | 0 | kg |  | 0
0
[10 empty] | Q4= | Agent (+Ventilation Comp.) |  | 2793 | kg
Anticipated Tempreture |  | 28 |  | °C | 0 | [5 empty] | Compensated Agent |  | 0 | kg
No temperature compensation required
Over Design |  | No |  |  | 0
Over Design Percent |  | 0% |  | % | [6 empty] | Agent |  | 0 | kg
[10 empty] | Q5 (Total) = | Total Agent (CO2) |  | 2793 | kg
[11 empty] | Number of CO2 Containers |  | 63
Reserve (100%) |  | No |  |  | 0 | [5 empty] | Agent |  | 0 | kg
[10 empty] | Q5 (Total) = | Total Agent (CO2) |  | 2793 | kg
[11 empty] | Number of CO2 Containers |  | 63
Just Main Cylinders
ATTENTION
"NFPA 12 (2011 Edition): 5.4.1.1 After the design concentration is reached, the concentration shall be maintained for a substantial period of time, but not less than 20 minutes."
Note on A17: Ali: for DEEP SEATED fire select appropriate design concentration maually
Note on A19: Ali: for DEEP SEATED fire, flooding factor shall be selected manually
Note on L19: Ali: for SURFACE fire appropriate flooding factor will be select automatically for each enclosure seperatly!
Note on D22: You can select 5 parts for each sector that extinguish simultaneous (calculation will be perfored based on involved enclosure who that you selected): 1-Main Area 2-Main Area & Suspend Ceiling 3-Main Area & Suspend Ceiling & Rised Floor 4- Other Part 5- Other Part for each part, you have to insert its data to corrected sheet.
Note on K25: Ali: NFPA 12 (2011 Edition), 5.3.3.1: In figuring the net cubic capacity to be protected, due allowance shall be permitted to be made for permanent nonremovable, impermeable structures materially reducing the volume.
Note on L25: Ali: Total Hazard Volume after deducing non-permeable volume
Note on O37: Ali: According to: NFPA 12 (2011 Edition), Table 5.3.2.2 Minimum Carbon Dioxide Concentrations for Extinguishment
Note on A43: Ali: NFPA 12, Material Conversion Factor shall be selected manually from FIGURE 5.3.4 BS 5306 - 4, Material Conversion Factor selected Automatically
Note on D43: Ali: NFPA Material Conversion Factor shall be selected manually
Note on E43: Ali: BS Material Conversion Facotr
Note on A48: Ali: Inser Data in "Leakage Compensation" pag manually Unclosable Opening NFPA 12, 5.3.5.1
Note on D48: Ali: Manually Insert Data Please go to "Leakage Compensation" for calculating
Note on A55: Ali: NFPA 12, 5.3.5.2
Note on A63: Ali: NFPA 12, 5.3.5.3 & 5.3.5.4
Note on M73: Ali: 67 Litre Cylinder contain 45kg CO2
Note on M81: Ali: 67 Litre Cylinder contain 45kg CO2

## Flow rate
[18 empty] | Date: | 1396/05/28
[18 empty] | Revision | 26.8
Ali Cheraghi
CO2 Fire Suppression System
Total Flooding method | [20 empty] | back to Protected Areas
Project Name Sample
Type of Fire |  | Deep Seated
Discharge Time |  | 7 min. (30% in 2 min.) |  | min. | NFPA 12, 5.5.2.3: For deep-seated fires, the design concentration shall be achieved within 7 minutes, but the rate shall be not less than that required to develop a concentration of 30 percent in 2 minutes. (30% = 0,67 kg/m³).
Discharge Time |  | 8 |  | min.
Discharge Time |  | FALSE
Number of Enclosures |  |  | 3 | [12 empty] | Total Volume |  | 2100 | m3 | FALSE
[16 empty] | Total Agent |  | 2793 | kg | 0
Sector No. | Hazard Name |  |  | Length | Width | Height | Area | Total Volume | Percent of Volume / Total | Basic Aget Quantity/Hazard | Total Aget Quantity/Hazard | System Flow Rate | Main Pipe Size Estimating | Flow rate / Hazard | Number of Nozzle |  | Agent/ Nozzle | Flow Rate / Nozzle | Nozzle Branch Pipe Size Estimating
[15 empty] | recommend | set to
|  |  |  | m | m | m | m2 | m3 | % | kg | kg | kg/min. |  | kg/min. | pcs | pcs | kg | kg/min. | kg/min.
1 | Switchgear Room |  |  | 30 | 10 | 5 | 300 | 1425 | 67.86% | 1895.25 | 1895.25 | 837.9 | 2 1/2″ (65 mm) | 236.9062 | 10 | 12 | 157.9375 | 19.7422 | 1/2″ (15 mm) | 837.9
2 | Transformer Room |  |  | 5 | 3 | 5 | 15 | 75 | 3.571% | 99.75 | 99.75 |  |  | 99.75 | 1 | 2 | 49.875 | 6.2344 | 1/2″ (15 mm)
3 | Cable Gallery |  |  | 30 | 10 | 2 | 300 | 600 | 28.57% | 798 | 798 |  |  | 798 | 10 | 12 | 66.5 | 8.3125 | 1/2″ (15 mm)
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 |  |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 |  |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Pipe Size only can be as Estimating, Final Pipe Sizing shall be Carry out by Specialist Technicians via Tyco Software Programs.
For CO2 Total Flooding systems there are no strict rules governing the number of nozzles that should be applied to any type of hazard, however, nozzle spacing is dependent on the room height, flow rate, potential obstructions etc.
It is normally recommended that nozzles are uniformly positioned on the ceiling of an enclosure to ensure a satisfactory distribution of CO2.
Generally the nozzles have a maximum coverage area of 30 square metres in a room up to 5 metres high
Some rules and our recommendations: 1) position the nozzles uniformly on the ceiling 2) 30 m² coverage max. 3) 6 m spacing between nozzles 4) 3 m spacing between walls/obstructions and nozzles 5) 5 m coverage height
Vds 2093, 7.2.2: For total flooding systems the maximum protected area per nozzle shall not exceed 30m².
Vds 2093, 7.2.3: In rooms higher than 5m the nozzles providing general CO2 distribution shall not only be arranged in the upper part under the ceiling of the room to be protected, but also at approx. 1/3 of the room height. The lower nozzles shall discharge approx. 35% of the required CO2 design quantity into the flooding zone. The protection of rooms higher than 10m and areas for which an extended discharge is provided shall be agreed with the competent authority.
Note on Q19: Ali: Set Number of Nozzles Manually for each hazard

## D.S. - D.C. & F.F.
CO2 Fire Suppression System
Total Flooding method | [6 empty] | back to Protected Areas
(Deep Seated Fires)
NFPA 12 (2011 Edition) Table 5.4.2.1 Flooding Factors for Specific Hazards
Insert Project Name Sample
Your Data Selection:
Total Volume | 2100 | m 3 |  | Design Concentration | 50 | %
|  |  |  | Flooding Factor | 1.33 | kg CO2/m3
Select appropriate Design Concentration & Flooding Factor Manually and Insert data in Protected Area Sheet
Total Volume Enclosure 1 |  | 1425 |  | Volume Factor 1 | 0.74 | Kg Co2/m3
Total Volume Enclosure 2 |  | 75 |  | Volume Factor 2 | 0 | Kg Co2/m3
Total Volume Enclosure 3 |  | 600 |  | Volume Factor 3 | 0 | Kg Co2/m3
Total Volume Enclosure 4 |  | 0 |  | Volume Factor 4 | 0 | Kg Co2/m4
Total Volume Enclosure 5 |  | 0 |  | Volume Factor 5 | 0 | Kg Co2/m5
Hazard Factors
Hazard |  |  |  | Design Concentration ( % ) | Flooding Factor ( kg CO2/m3 )
Electrical Equipment |  | Enclosed Rotating Equipment. Dry Electrical Wiring. Electrical Insulating Materials. | Spaces 56.6 m3 | 50 | 1.6
|  |  | Spaces greater than 56.6 m3 | 50 | 1.33
Electronic Data Processing Installation |  | Central Processing Area & Equipment. |  | 53 | 1.5
|  | Data Processing.Tape Controlled Machinery & Tape Storage. Service Voids. |  | 68 | 2.25
Stores |  | Record ( Bulk Paper ) Storag , Archives For Paper Documents , Dust & Covered Trenches |  | 65 | 2
|  | Fur Storage Vaults. Dust Collectors. |  | 75 | 2.66
The Table Based on an expantion ratio of .53 m3/kg at a temperature of 10 'C

## S.F. - F.F.
CO2 Fire Suppression System
Total Flooding method | [6 empty] | back to Protected Areas
(Surface Fires)
NFPA 12 (2011 Edition) Table 5.3.3(b) Flooding Factors (BS 5306-4, Table 1)
This Page is incorrect Field, You Selected Deep Seated Fires Field but This Field is acoording to Surface Fires
5.3.3.2.1, In two or more interconnected volumes where free flow of carbon dioxide can take place, the carbon dioxide quantity shall be the sum of the quantities calculated for each volume, using its respective volume factor from Table 5.3.3
Total Volume | 0 |  | Volume Factor |  | 0 | Kg Co2/m3
Total Volume Enclosure 1 | 0 |  | Volume Factor 1 |  | 0 | Kg Co2/m3
Total Volume Enclosure 2 | 0 |  | Volume Factor 2 |  | 0 | Kg Co2/m3
Total Volume Enclosure 3 | 0 |  | Volume Factor 3 |  | 0 | Kg Co2/m3
Total Volume Enclosure 4 | 0 |  | Volume Factor 4 |  | 0 | Kg Co2/m4
Total Volume Enclosure 5 | 0 |  | Volume Factor 5 |  | 0 | Kg Co2/m5
Volume Factor NFPA 12 (2011 Edition) - Table 5.3.3
Volume of Space | Volume Factor |  |  | Calculated Quantity of CO2
m3 | m3 / Kg Co2 | Kg Co2 / m3 |  | Kg
Volume < 3.96 | 0.86 | 1.15 |  | 0
3.96 < Volume < 14.15 | 0.93 | 1.07 |  | 4.5
14.16 < Volume < 45.28 | 0.99 | 1.01 |  | 15.1
45.29 < Volume < 127.35 | 1.11 | 0.9 |  | 45.4
127.36 < Volume < 1415.0 | 1.25 | 0.8 |  | 113.5
Volume > 1415.0 | 1.37 | 0.74 |  | 1135

## S.F. - D.C (NFPA)
CO2 Fire Suppression System
Total Flooding method |  |  |  |  | A | 0.0098
(Surface Fires) |  |  |  | go to Material Conversion Factor Curve | B | -0.052
NFPA 12 (2011 Edition) Table 5.3.2.2 |  |  |  | back to Protected Areas | C | 1.626
This Page is incorrect Field, You Selected Deep Seated Fires Field but This Field is acoording to Surface Fires
Minimum Carbon Dioxide Concentrations for Extinguishment
Material | Theoretical Minimum Co2 Concentration ( % ) | Minimum Design Co2 Concentration ( % ) | Material Conversion Factor (NFPA 12)
Acetylene | 55 | 66 | Selected Manually From "Materiaal Conversion Factor Curve
Acetone | 27 | 34
Aviation Gas Grades 115 / 145 | 30 | 36
Benzol, benzene | 31 | 37
Buta diene | 34 | 41
Butane | 28 | 34
Butane-I | 31 | 37
Carbon Disulphide | 60 | 72
Carbon monoxide | 53 | 64
Coal gas or natural gas | 31 | 37
Cyclopropane | 31 | 37
Diethyl Ether | 33 | 40
Dimethyl Ether | 33 | 40
Dowtherm | 38 | 46
Ethane | 33 | 40
Ethyle Alcohole ( Ethanol ) | 36 | 43
Ethyle Ether | 38 | 46
Ethylene | 41 | 49
Ethylene dichloride | 21 | 25
Ethylene oxide | 44 | 53
Gasoline | 28 | 34
Hexane | 29 | 35
Higher Paraffin Hydrocarbon | 28 | 34
Hydrogen | 62 | 75
Hydrogen Sulfide | 30 | 36
Isobutane | 30 | 36
Isobutylene | 26 | 34
Isobutyl formate | 26 | 34
JP 4 | 30 | 36
Kerosene | 28 | 34
Methane | 25 | 34
Methyl Acetate | 29 | 35
Methyl Alcohole ( Methanol ) | 33 | 40
Methyl Butene - I | 30 | 36
Methyl Ethyl Ketone | 33 | 40
Methyl Ethyl formate | 32 | 39
Pentane | 29 | 35
Propane | 30 | 36
Propylene | 30 | 36
Quenching, lubricating oils | 28 | 34
Note on A32: CnH2m + 2m - 5

## S.F. - MCF
CO2 Fire Suppression System
Total Flooding method |  |  | back to Design Concentration Sheet
(Surface Fires)
NFPA 12 (2011 Edition) FIGURE 5.3.4 Material Conversion Factors |  |  | back to Protected Areas
This Page is incorrect Field, You Selected Deep Seated Fires Field but This Field is acoording to Surface Fires
Select Type of Fule | Methane
Min. Design Concentration | 34 | %
NFPA 12, 5.3.4 Material Conversion Factor: For materials requiring a design concentration over 34 percent, the basic quantity of carbon dioxide calculated from the volume factor given in Table 5.3.3 shall be increased by multiplying this quantity by the appropriate conversion factor given in Figure 5.3.4.
Back

## S.F. - D.C (BS)
CO2 Fire Suppression System
Total Flooding method
(Surface Fires)
BS 5306-4 Table 2 |  |  | back to Protected Areas
This Page is incorrect Field, You Selected Deep Seated Fires Field but This Field is acoording to Surface Fires
Minimum Carbon Dioxide Concentrations for Extinguishment
Material | Minimum Design Co2 Concentration ( % ) | Material Conversion Factor (BS5839-4, Table 2)
Acetylene | 66 | 2.5
Acetone | 34 | 1
Benzol, benzene | 37 | 1.1
Butane | 34 | 1
Butane-I, 3-diene | 37 | 1.3
Carbon Disulphide | 72 | 3
Carbon monoxide | 64 | 2.4
Coal gas or natural gas | 37 | 1.1
Cyclopropane | 37 | 1.1
Diethyl Ether | 40 | 1.5
Dowtherm | 46 | 1.5
Ethane | 40 | 1.2
Ethyle Alcohole ( Ethanol ) | 43 | 1.3
Ethylene | 49 | 1.6
Ethylene dichloride | 25 | 1
Ethylene oxide | 53 | 1.75
Hexane | 35 | 1.1
Hydrogen | 75 | 3.3
Isobutane | 36 | 1.1
Kerosene | 34 | 1
Methane | 34 | 1
Methyl Alcohole ( Methanol ) | 40 | 1.2
Pentane | 35 | 1.1
Petroleum Spirit | 34 | 1
Propane | 36 | 1.1
Propene | 36 | 1.1
Quenching, lubricating oils | 34 | 1

## Temp. Compensation
CO2 Fire Suppression System
Total Flooding method | [8 empty] | back to Protected Areas
NFPA 12 (2011 Edition) Tempreture Compensation
Insert Project Name Sample
5.3.5.3 For applications where the normal temperature of the enclosure is above 200°F (93°C), a 1 percent increase in the calculated total quantity of carbon dioxide shall be provided for each additional 5°F (2.8°C) above 200°F (93°C). 5.3.5.4 For applications where the normal temperature of the enclosure is below 0°F (−18°C), a 1 percent increase in the calculated total quantity of carbon dioxide shall be provided for each degree Fahrenheit below 0°F (−18°C).
Hazard temperature > 93°C ( 200 °F ) : 1% increase of calculated CO2 quantity for each additional 2.8°C above 93°C.
|  |  |  | CO2 high temp. | 0 | °C
Temperature | 28 | °C | NO Additional Quantity of Co2 Require |  |  |  | 0 | Kg
Hazard temperature < -18°C ( 0 °F ) : 1% increase of calculated CO2 quantity for each additional 1°C below -18°C.
|  |  |  | CO2 Low temp. | 0 | °C

## Leakage Compensation
CO2 Fire Suppression System
Total Flooding method | [11 empty] | back to Protected Areas
NFPA 12 (2011 Edition) 5.3.5.1, Openings That Cannot Be Closed. | [11 empty] | go to Laeakage Rate
Insert Project Name Sample
NFPA 12, 5.2.1.2 If the quantity of carbon dioxide required for compensation exceeds the basic quantities required for flooding without leakage, the system shall be permitted to be designed for local application
NFPA 12, 5.3.5.1.1: Any openings that cannot be closed at the time of extinguishment shall be compensated for by the addition of a quantity of carbon dioxide equal to the anticipated loss at the design concentration during a 1-minute period.
NO Additional Quantity of CO2 Required for Compensation
1
H: Opening centered from below ceiling |  | 0 | m | Leakage Rate |  | 0 |  | kg/min·m2 | Total Basic CO2 Quantity | 2793 | Kg
A: Leakage Area |  | 0 | m 2 |  | #REF! |  | 1 |  | Co2 Opening Loss | 0 | Kg
ATTENTION
" The Concentration Should be Maintain for 20 Minutes "
H
A
Note on A13: (Reference NFPA 12 Chapter 2 - 2.3 ) (Reference Clause 15.2 of BS 5306 : Part 4)
Note on H13: Ali: selected manually

## Leakage Rate
CO2 Fire Suppression System
Total Flooding method |  |  |  |  | back to Protected Areas
(Deep Seated Fires)
NFPA 12 (2011 Edition) 5.3.5.1, Openings That Cannot Be Closed. |  |  |  |  | back to Leakage Compensation
Insert Project Name Sample
Deep Seated Fire
| Design Concentration | 50 | %
|  | m |  | ft
| H: Opening centered from below ceiling | 0 | Convert | 0
|  | Lb/min·ft2 |  | kg/min·m2
| Enter Leakage Rate | 0 | Convert | 0
H
A
Uncloseable Opening